## Slide 1
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to attendees within two days.
How to Design a Centralized Vacuum System
Tim Dugan, P.E., Compression Engineering Corporation
Keynote Speaker
Sponsored by

## Slide 2: Q&A Format
Panelists will answer your questions during the Q&A session at the end of the Webinar.
Please post your questions in the Questions Window in your GoToWebinar interface.
Direct all questions to Blower & Vacuum Best Practices Magazine
Sponsored by

## Slide 3: Handouts

## Slide 4: Disclaimer
All rights are reserved. The contents of this publication may not be reproduced in whole or in part without consent of Smith Onandia Communications LLC. Smith Onandia Communications LLC does not assume and hereby disclaims any liability to any person for any loss or damage caused by errors or omissions in the material contained herein, regardless of whether such errors result from negligence, accident, or any other cause whatsoever.
All materials presented are educational. Each system is unique and must be evaluated on its own merits.

## Slide 5
Introduction by Rod Smith, Publisher
Blower & Vacuum Best Practices Magazine
Sponsored by
How to Design a Centralized Vacuum System

## Slide 6: 2019 Best Practices EXPO & Conference

## Slide 7: 2019 Best Practices EXPO & Conference
The conference will focus on sustainable on-site utilities powering automation including compressed air, blower, vacuum and cooling systems. Presentations should encompass one or more of these themes.
Call for Abstracts
  Abstract submissions are due Friday, March 29, 2019.
  Speakers receive a complimentary Conference Pass, a $675 value!
  To submit an abstract, please visit
  cabpexpo.com/conference/speakers
Quality & Safety Management
Facility Maintenance & Reliability
Energy Savings / IoT Monitoring
Water Savings / Energy Management

## Slide 8: About the Speaker
President and Principal Engineer, Compression Engineering Corporation
Over 25 years of experience in the industry
Sponsored by
Tim Dugan, P.E.
Compression Engineering Corporation

## Slide 9: How to Design a Centralized Vacuum System
March 14, 2019 Tim Dugan, P.E.
Compression Engineering Corporation

## Slide 10: Outline
Determine Consolidated System Vacuum Level
Determine Demand at That Vacuum Level
Size Vacuum Pump(s)
Size Piping Header
Size receiver
Design Controls

## Slide 11: Determine Consolidated System Vacuum Level
Start at the processes, and work your way back
For pressure-critical process, determine needed VACUUM and calculate the FLOW
For flow-critical process, determine the FLOW necessary and calculate the VACUUM
Vacuum is proportional to flow at less than 15”Hg.
Ideally, measure with a flow meter and vacuum gauge.
Some low-cost thermal mass flow meters can work.
This can be done analytically with a detailed audit.

## Slide 12: Determine Consolidated System Vacuum Level
Build a table:
23”Hg is the required common vacuum level AT THE PROCESS.

## Slide 13: Determine Consolidated System Vacuum Level
What level at the VACUUM PUMP(s)?
Two allowances need to be added:
Pipe restriction allowance - use 1.0”Hg.
Control band allowance – start with +/- 1”Hg for VFD, +/- 2”Hg for start-stop.
For this example, let’s use start-stop. So now, we have an average level of 23+1+2 = 26”Hg for the pump inlets.

## Slide 14: Determine Demand at That Vacuum Level
First, calculate new total mass flow, or scfm.
Vacuum influences mass flow, and vice-versa.
For the demands that are less than 15”Hg, increasing vacuum to 25”Hg will not increase mass flow
For the demands that are less than 15”Hg, they will increase, up to 15”Hg, by the square root:
New demand = (15/current vac)^0.5 x mass flow at current vac

## Slide 15: Determine Mass Flow at That Vacuum Level
But vacuum pumps are rated in “icfm” (or “acfm”), volume flow at intake, so you can’t size pumps yet!
Adjusted mass flow and summed mass flow:

## Slide 16: Determine Peak Demand at That Vacuum Level
Calculate icfm from scfm and vacuum:
icfm = scfm x Pamb / (Pamb – Vac) – neglecting temperature effect
Note that Process D dominates the flow requirement.
These are PEAK flows.

## Slide 17: Size Vacuum Pump(s)
Let’s add production utilization numbers before we size pumps.
Some demands are constant and some are not.
In fact, it’s quite “peaky” in this example

## Slide 18: Determine Average Demand at That Vacuum Level
To simplify, just calculate WEIGHTED AVERAGE FLOW.
This is more accurately done in an audit.

## Slide 19: Size Vacuum Pump(s)
Huge variance - 56 icfm base to 382 icfm 5-10% of the time.
One VFD would not cover the range, and no backup.
Multiple smaller fixed-speed vacuum pumps recommended.
Add safety margin to the total peak flow, 450 icfm.
Use “N+1” design with a good split for following the demand.
A four-plex 150 icfm/ea set is recommended.
A duplex is oversized and inefficient at low demand.
Two VFDs are an alternative, but in reality you would need three to have a back-up.

## Slide 20: Size Vacuum Pump(s)
A common vacuum pump for this size is a lubricated vane type.
One suppliers’ curve set is below:
26”Hg = 100 Torr
150 acfm

## Slide 21: Size Piping
Recall our piping pressure drop “allowance” is 1.0”Hg.
Use a pressure drop calculation tool like https://www.checalc.com/fluid_flow_fitting_losses.html

## Slide 22: Size Piping

## Slide 23: Size Receiver
For energy efficiency, master controls need to work.
Pumps have to start and stop to follow demand.
Which requires STORAGE
This vacuum pump is a 10hp. Start-stop frequency is the issue we are trying to manage with receiver sizing. 10 starts/hr is OK for this hp.
We calculated that a 2,000 gal tank is needed with a +/-2”Hg control band.
Small tanks end up with wide delta Ps and constant-running pumps.

## Slide 24: Size Receiver

## Slide 25: Design Controls
With a 4-plex, you must have a master controller.
I recommend a “target” algorithm if it is available.
The “trim” vacuum pump should run at the target +/- half of the control band.
“Cascade” not preferred – too wide of delta P.
The “base” pumps run at 100%.
Tune for actual demand changes, not just steady-state.

## Slide 26: Summary
Determine Consolidated System Vacuum Level
Determine Demand at That Vacuum Level
Size Vacuum Pump(s)
Size Piping Header
Size receiver
Design Controls

## Slide 27: About the Speaker
Systems Engineering Manager, Busch USA
Over 17 years of experience in the industry
VJ Gupta
Busch USA

## Slide 28
Sizing an Optimum Central Vacuum Solution
Webinar: How to Design a Centralized Vacuum System
VJ Gupta, Systems Engineering Manager
March 14, 2019
Page 1

## Slide 29
Central Vacuum Systems
Why Centralize?
Return on
Investment (ROI)
Uptime Improvements
Utility Savings
Process Efficiency
Environmentally
Friendly
Plant Expandability
Page 2

## Slide 30
Central Vacuum Systems
Applications
Pick and Place
Molding / Forming
Pneumatic Conveying
Vacuum Packaging
Pharmaceutical Processing
House Vacuum
Applications
for Central Systems!
Page 3

## Slide 31
Central Vacuum Systems
Assessing the Vacuum Application
Visit customer’s plant!
Number of machines using vacuum?
Vacuum level on each machine?
Is their vacuum process dynamic, static or both?
Data logging of vacuum level, fluid temperatures etc.
Page 4

## Slide 32
Central Vacuum Systems
Determine Customer Needs
Energy rebates realized
Floor space
Faster pump down time
Continuous vacuum demand
Processes with different vacuum levels
High noise levels
Page 5

## Slide 33
Vacuum Equipment Optimization
5-Elements of Efficiency
Selecting the most suitable pump technology for the process is crucial to performance, efficiency and total life costs.
During operation, vacuum pumps convert kinetic energy into heat energy. Heat recovery systems can harness this energy.
Efficient operation of vacuum processes requires experience in the interaction of all process components.
A central vacuum supply offers the potential to reduce operating costs and increase energy efficiency.
Control of vacuum systems finely tuned to production ensures optimum process stability and output.
Page 6

## Slide 34
Design Considerations
Different Vacuum Levels
Process 1
50 acfm
10”HgV
Pump 1
Pump 2
Process 2
50 acfm
20”HgV
 | Pumping Capacity (acfm)
Process 1; at 10”HgV | 50
Process 2; at 20”HgV | 50
Process 1 + Process 2; at 20”HgV | 
150
100 ?
Why is this important?
It is common to have processes within a plant to have significantly different vacuum levels.
Vacuum centralization should be done only where it makes sense! Sometimes, Point-of-Use (POU) pumps are better suited.
Page 7

## Slide 35
Design Considerations
Pressure Drop
Process or
Machinery
Vacuum Pump
What is the requirement here?
P1V1 = P2V2
Need 144 ACFM @ 26.5”HgV
Why is this important?
Pressure drop directly affects pump size and power consumption.
Vacuum centralization is not just about the pump.
ΔP = 1.5”Hg
Requirement here = 100 ACFM @ 25”HgV
Page 8

## Slide 36
Design Considerations
To VSD or Not to VSD?
Why is this important?
VSD is not the solution for all applications.
Multiple fixed speed pumps offer simplicity, higher efficiency and redundancy.
Process 1
50 ACFM
20” HgV
Pump
2nd Pump
Process 2
50 ACFM
20” HgV
One Process Running
Two Processes Running
Pump Curve
Pump Curve
60
110
160
29.92"
20"
0"
Pumping Speed (ACFM) 

Vacuum (″ HgV)
Page 9

## Slide 37
Design Considerations
Sensor Location
Sensor on Process (away from pump)
Sensor on Vacuum Pump Suction
Why is this important?
Sensor provides real time feedback to VSD from a location that is critical to the process.
If sensor is installed at process, VSD can respond faster to demand changes.
VSD
Sensor
Vacuum Pump
Process
VSD
Sensor
Page 10

## Slide 38
Design Considerations
Buffer Tanks
Why is this important?
Centralizing applications with large flow requirements can generate significant vacuum spikes. VSD alone is unable to keep up!
Buffer tanks are a cost effective solution but must be sized correctly.
Vacuum Pump
Machines
Buffer Tank
Page 11

## Slide 39
Sizing an Optimum Central Vacuum Solution
Conclusion
Every Customer’s plant requirements are unique. Usually, there are different processes in one plant with different vacuum requirement levels.
Only centralize machines that make economical sense!
There is no “One Size Fits All” solution! An Optimal Centralized System is custom tailored to meet customer needs.
Conduct a complete study to determine customer requirements. Busch can help with this!
Consider all available options, i.e. various pump technologies, control schemes, buffer tanks, pipe header sizing, VSD etc.
Central systems can be a great solution but needs to be done right….
You need to work with an expert who can help with the detailed analysis and offers custom tailored solutions with minimal risks.
Page 12

## Slide 40
Sizing an Optimum Central Vacuum Solution
Contact Us
Thank you!
For more information about Busch Vacuum Pumps and Systems, please visit: www.buschusa.com
VJ Gupta
Systems Engineering Manager for Busch USA Office: (757) 502-7084 • Cell: (757) 373-0099 vj.gupta@buschusa.com
Page 13

## Slide 41
Please submit any questions through the Question Window on your GoToWebinar interface, directing them to Blower & Vacuum Best Practices Magazine. Our panelists will do their best to address your questions, and will follow up with you on anything that goes unanswered during this session.
Thank you for attending!
Q&A
Sponsored by
How to Design a Centralized Vacuum System

## Slide 42: Thank you for attending!
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to Attendees within two days.
Sponsored by

## Slide 43: 2019 Best Practices EXPO & Conference

## Slide 44: 2019 Best Practices EXPO & Conference
The conference will focus on sustainable on-site utilities powering automation including compressed air, blower, vacuum and cooling systems. Presentations should encompass one or more of these themes.
Call for Abstracts
  Abstract submissions are due Friday, March 29, 2019.
  Speakers receive a complimentary Conference Pass, a $675 value!
  To submit an abstract, please visit
  cabpexpo.com/conference/speakers
Quality & Safety Management
Facility Maintenance & Reliability
Energy Savings / IoT Monitoring
Water Savings / Energy Management

## Slide 45
Thursday, April 4, 2019 – 2:00 PM EST
Register for free at
www.airbestpractices.com/magazine/webinars
Loran Circle
Circle Training & Consulting
Keynote Speaker
April 2019 Webinar Safety and Quality in Compressed Air: Why You Should Care
Sponsored by